{"text_format":"2","workbook":"xlsx","n_sheets":3,"sheets":["Generacion","Proyectos ","Eficiencia"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":16,"defined_names":398,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Generacion","index":0,"n_rows":124,"n_cols":15,"rows_kept":124,"cut":false,"hidden":false,"merged":[]}
[]
[]
[]
["GENERACION (MWh)"]
[]
[]
[null,null,2005,2006,2007,2008,2009,2010,2011,2012,2013,2014,2015,2016,2017]
["CENTRALES HIDROELECTRICAS"]
["CORANI","COR1234",250663.52100000001,323312.78000000003,314017.66700000007,345890.46,326422.41800000001,280767.663,317689.14,325459.11999999994,373791.26,371305.77999999997,377176.696,214629.93900000001,284284.71100000001]
["SANTA ISABEL","SIS12345",376807.11,481031.12,469991.93699999992,515827.09000000008,490869.35499999998,418380.17099999997,477614.6,485267.32000000007,555713.26,552076.43999999994,560551.92799999996,330698.88400000002,431404.26799999998]
["ZONGO","ZON1",9930.85,11805.46,9633.5199999999986,10130.629999999999,10722.61,11345.115999999998,11062.147000000001,9730.2360000000008,8366.9229999999989,9230.8360000000011,9970.2779999999984,9497.0040000000008,10212.421999999999]
["TIQUIMANI","TIQ1",10838.780000000002,15201.09,14321.560000000001,11831.330000000002,12186.210000000001,8884.2089999999989,15926.226000000001,12913.739999999998,11358.185999999998,10445.099,12813.867,6632.0620000000017,11241.978999999999]
["BOTIJLACA","BOT1",7618.75,9594.16,10530.88,8233.340000000002,7295.7800000000007,7849.8739999999998,8621.2659999999996,8717.6899999999987,8548.19,6937.6459999999988,8959.4909999999982,5032.6009999999997,8563.4409999999989]
[null,"BOT2",6501.2400000000007,8432.23,9131.5700000000015,7920.81,6980.7,6640.692,7153.3130000000001,7359.0120000000006,7028.0189999999984,5548.0110000000004,7037.5190000000011,3451.9039999999995,6239.6179999999995]
[null,"BOT3",19045.099999999999,23242.400000000001,22072.449999999997,19375.100000000002,22324.54,21561.253000000001,20814.348000000002,22706.515999999996,22174.722999999998,20967.522999999997,23605.780999999999,18889.346000000001,20402.677000000003]
["CUTICUCHO","CUT1",8059.9999999999991,10975.14,8737.5400000000009,6715.3899999999994,8969.89,7186.3240000000005,9743.3469999999998,9415.1349999999984,6458.4300000000012,5475.3140000000012,14181.028999999999,4440.6810000000005,9498.8819999999996]
[null,"CUT2",8028.7800000000007,10715.81,9869.869999999999,5407.15,8904.2599999999984,6993.1389999999992,9282.0769999999993,8698.5240000000013,5753.3399999999992,4912.893,12898.888999999999,5619.9069999999992,9023.6689999999999]
[null,"CUT3",7920.7800000000007,10014.33,9512.64,4785.76,8626.3799999999992,6822.6170000000011,9067.5030000000006,8820.1739999999991,6045.0469999999987,5060.7860000000001,13386.753999999999,5422.3110000000006,8865.5539999999983]
[null,"CUT4",6145.670000000001,7658.0700000000015,6933.9699999999993,4001.69,6429.079999999999,5297.4830000000002,6581.7929999999997,6336.6400000000012,4570.0379999999996,3245.1849999999999,6687.3670912745001,2561.4390000000003,4531.527000000001]
[null,"CUT5",76307.790000000008,82935.860000000015,95055.06,89647.709999999992,91460.58,90321.68,94885.142000000007,92591.819999999992,80968.934000000008,71783.653000000006,80462.043000000005,75993.778999999995,96164.228000000003]
["SANTA ROSA","SRO1",0,15731.59,39484.22,33075.410000000003,35626.61,35381.828000000001,40391.101000000002,32300.107999999997,36699.025999999998,35041.322,38808.311000000002,27181.951999999997,38544.047999999995]
[null,"SRO2",0,14909.620000000003,39728.770000000004,32947.730000000003,22743.23,43128.714000000007,46044.358999999997,43194.46,45291.724999999999,48557.090000000004,47305.845000000001,39690.658000000003,47225.397999999994]
["SAINANI","SAI1",58292.920000000006,53811.209999999992,69811.37999999999,65572.81,64284.599999999991,66898.476999999999,71701.509999999995,68123.947000000015,70554.083999999988,15429.729000000001,23543.032999999996,53982.859000000004,69211.264999999999]
["CHURURAQUI","CHU1",59206.030000000006,61979.909999999996,69616.5,63259.600000000006,65835.640000000014,63528.492000000006,66072.78,69551.442999999999,71908.643000000011,64762.602000000014,71255.490000000005,53061.766000000011,68171.011999999988]
[null,"CHU2",59545.58,61029.9,68033.11,61633.520000000004,62954.649999999994,62589.967000000004,67733.377999999997,64736.137999999999,72200.594999999987,62725.933999999994,67719.197,53897.992999999995,66329.928]
["HARCA","HAR1",77742.790000000008,79606.670000000013,83067.34,76648.87,76645.84,79080.590999999986,83215.97,78452.136999999988,86076.892000000022,78528.325000000012,81849.416999999987,63047.572,79535.85500000001]
[null,"HAR2",76744.5,78841.329999999987,82261.419999999984,74650.569999999992,72829.819999999992,77042.933999999994,78275.415999999997,73415.542000000016,79960.05799999999,77429.541999999987,80452.606,61868.472999999998,81530.162000000011]
["CAHUA","CAH1",79504.53,82057.62,38406.979999999996,75324.36,80098.12000000001,79039.576000000001,58254.008999999998,51281.207999999999,86457.891000000003,85493.885999999984,81648.601999999999,62691.474999999999,85854.238000000012]
[null,"CAH2",75479.470000000016,80324.78,94275.939999999988,69349.11,81575.399999999994,81435.836999999985,91507.437000000005,83285.340000000011,84764.018000000011,77185.930999999997,81079.112999999998,67549.632999999987,83617.593000000008]
["HUAJI","HUA1",91921.260000000009,88960.9,101507.48999999999,92363.880000000019,89014.59,95760.286999999982,95144.05,95119.72,105447.58899999999,99009.819000000003,86632.661000000007,79958.990999999995,91011.156999999992]
[null,"HUA2",91866.189999999988,89080.53,99802.36,90380.57,85975.37999999999,93799.604999999996,98539.03,94138.09,99492.22,99241.433000000005,93811.007999999987,82387.252999999997,99447.379000000015]
["MIGUILLA","MIG1",3988.3999999999996,4594.78,4099.3999999999996,4237,4148,4114,4554.1049999999996,4812.643,4552.4240000000009,4384.4089999999997,4376.9049999999997,3466.1080000000002,4191.5759999999991]
[null,"MIG2",4252.7,4871.57,4226.8999999999996,4452,4241,4195,4563.4110000000001,4781.6249999999973,4698.2270000000008,4197.7930000000006,4145.2669999999998,3329.4500000000003,4038.616]
["ANGOSTURA","ANG1",11162.400000000001,13662.57,9623.6999999999989,7352.6,6375.1,9271.0999999999949,8656.5849999999991,10232.768999999998,8655.150999999998,8364.82,8059.2840000000015,8299.025999999998,7068.2120000000004]
[null,"ANG2",7167.1000000000013,8302.98,6129.2,4765,3943.8999999999996,4843.4999999999982,5139.1980000000003,4981.5259999999998,3998.6959999999999,4087.8379999999997,3992.585,2863.16,3531.5559999999991]
[null,"ANG3",null,null,null,3129.1600000000003,9101.7499999999982,5760.9160000000011,6575.5169999999998,7386.07,6891.6029999999992,6808.925000000002,6644.1160000000018,5656.7429999999995,6833.0870000000014]
["CHOQUETANGA","CHO1",12503.4,12874.77,12714.599999999997,12757,13858.9,12172.712,11726.216,12408.229999999998,12482.189999999999,11577.643,11539.983,9108.7590000000018,10812.361999999999]
[null,"CHO2",13041.700000000003,13001.180000000004,11545.9,10027.1,9926.27,14106.915000000001,13902.388999999999,15012.157999999999,15518.906999999997,14227.504000000001,14778.668000000003,11847.556,13785.387999999999]
[null,"CHO3",12662.7,13404.98,12082.900000000001,13597.999999999998,13581.15,11843.383000000002,11428.677,12088.935999999998,12150.215,11142.393000000002,11178.842000000001,9006.9719999999979,10677.777000000002]
["CARABUCO","CRB",40029.1,40546.71,35776.519999999997,42240.86,42325.619999999995,43231.955000000002,41999.478999999999,43164.040999999997,45495.326000000001,43258.477999999996,41867.756999999991,36040.239999999998,41074.044999999998]
["CHOJLLA Antigua","CHJ1y2",5819.0999999999995,249,1285,3684.2419999999997,5273.8789999999999,5956.3567500000081,3270.2496729999998,5549.0742733333336,3766.9215449999997,4567.3325349999996,1658.2380349999999,38.668450000000043,0]
["CHOJLLA","CHJ",109893.09999999999,91555.531999999992,131993.4,115486.92299999997,119762.48675236771,106123.25798427663,124388.162,135330.64200000002,141958.08270668716,127364.10300000003,130614.54000000001,50256.089999999975,127227.77000000002]
["YANACACHI","YAN",179704.90000000002,131842.29999999999,215556.69999999998,197562.09999999992,197753.89600000007,190812.26330156953,206067.00099999999,209706.07100000003,223487.34744793986,70571.212,211398.55300000001,155757.26200000002,179334.13099999996]
["KANATA","KAN1",16270.12,21465.119999999995,17209.439999999999,20475.7,15643.88,14119.3,19288.97,20815.78,16358.64,19804.840000000004,17612.39,12031.66,10963.130000000001]
["KILPANI","KIL123",37321.43,40620.410000000003,34983.023000000001,38273.64,40036.68,40270.455000000002,38528.400999999998,41587.581999999995,42148.481999999996,45154.620999999999,41357.006000000001,32860.883000000002,31306.786999999997]
["LANDARA","LAN123",15924.050000000001,18042.919999999998,15634.244000000002,16792.52,17601.849999999999,14596.415000000001,17363.156999999999,17535.357,18995.719000000001,22123.662000000004,18022.292999999998,14087.349,14473.441999999999]
["PUNUTUMA","PUN1",13169.609999999999,15066.42,14616.29,17274.629999999997,17051.010000000002,16964.522000000001,17331.444,18585.001000000004,16688.195999999996,17786.664000000001,18207.585999999999,16078.901000000002,15005.555]
["QUEHATA","QUE01",null,null,949.73,3406.07,4897.1899999999996,3310.3999999999996,4002.56,6492.8999999999987,7388.4,7175.8399999999992,8301.2000000000007,2307.6,3547]
[null,"QUE02",{"$nulls":6},51.81,346.79999999999995,0,0,null,2352.1,3707.2000000000003]
["SAN JACINTO","SJA01",{"$nulls":10},2118.4740000000002,5921.3628000000017,9940.8974000000035]
[null,"SJA02",{"$nulls":10},1880.5391999999999,6106.0889999999999,10262.133000000002]
["MISICUNI","MIS",{"$nulls":12},11172.225999999999]
["PARQUES EÓLICOS"]
["QOLLPANA","QOL Fase I",{"$nulls":8},36.528500000000001,8157.7569999999996,11450.126,13207.373,12488.579]
[null,"QOL Fase II",{"$nulls":11},21704.071000000004,47894.7]
[]
["PLANTAS SOLARES"]
["YUNCHARA","YUN",{"$nulls":12},1065.63625]
[]
["CENTRALES TERMOELECTRICAS"]
["GUARACACHI","GCH01",26164.400000000001,50038.400000000001,19400,18837.2,74126.778671406006,54977.579999999987,31424.37,44186.280000000006,6585.9599999999991,15638.4,14091.300000000003,42919.199999999997,41459.700000000004]
[null,"GCH02",13563.6,25189.599999999999,8818.4000000000015,12728.324999999999,55177.356636180994,44343.569999999992,38362.5,31007.909999999996,4921.4399999999996,14575.08,10209.6,28229.760000000002,20603.039999999997]
[null,"GCH04",230.67,9953.8760000000002,2160.1340000000005,4707.2579999999998,34079.316408226761,35434.590000000004,65185.067999999999,40516.368000000002,17730.18,24451.464,13814.243999999999,43634.928000000007,24144.995999999996]
[null,"GCH06",8340.8999999999978,20173.900000000001,5527.5,8419.2620000000279,42803.138590336945,47583.179999999993,73021.77,79926.345000000001,32721.119999999995,52400.755703329996,49910.714999999997,73438.604999999996,47740.184999999998]
[null,"GCH09",345725,354602.80700000003,335472.45600000006,383101.16399999993,280808.80416330742,304167.35200000001,362328.33600000001,345670.74,479429.598,420127.47135156026,459226.69199999992,240047.45999999993,381288.42]
[null,"GCH10",350449.69800000009,346771.51500000001,308409.01799999998,353846.016,338845.1554794985,274064.72799999994,328187.05200000003,425317.902,461289.34800000006,412122.105063011,378806.54399999999,386168.79599999997,365210.38799999998]
[null,"GCH11",null,null,265514.63500000001,391554.18374999997,425665.0024,386364.63308200007,362853.24075,215762.25825000004,201328.714125,301526.55250000005,234237.29225000003,299524.30199999997,149744.47925]
[null,"GCH12",{"$nulls":5},85.295999999999992,1236.1020000000001,369449.51400000002,616226.28899999999,523552.59600000002,544179.25994216464,222713.652,361213.69200000004]
["SANTA CRUZ","SCZ01",44503.499999999993,64639.95,29439.65,44315.944999999992,69579.292000000001,73485.584999999992,82841.692500000005,69552.787499999991,23800.942902800001,44110.71,44085.419999999991,76414.35149999999,77133.690000000017]
[null,"SCZ02",88859.054999999993,94142.39999999998,52101.599999999991,70924.000000000015,58311.059500000003,86746.319999999992,105667.14,63985.62,16188.9,29892.711125046593,35185.5,69334.630499999999,64466.459999999992]
[null,"UNA01",{"$nulls":9},10615.624999999991,16947.507500000011,10655.049750000002,11162.566999999999]
["EASBA","SBU01",{"$nulls":11},708.84400000000005,751.15300000000002]
["ARANJUEZ","ARJ01",2015.7530000000002,515.04300000000001,211.90100000000001,1688.5209240000002,5851.9657339999994,0,1295.25873,6370.2055145175,1574.99368394,5457.5982823000022,903.1293569275839,2065.3987464399997,511.0025]
[null,"ARJ02",1659.729,508.69999999999993,158.71700000000001,1476.1726490000001,2175.5377950000002,7078.1761228214964,6630.8057900000003,0,0,1826.3282691160052,911.2479539279999,2494.435346064,148.19450000000001]
[null,"ARJ03",1409.6130000000001,506.46100000000001,127.95899999999997,1166.968429,2252.5128680000003,6933.803202000001,3921.550401,7512.4494400000012,1769.8755000000001,5453.1379999999999,742.68149999999991,3046.8119999999999,740.51250000000005]
[null,"ARJ08",106435.113,80957.54800000001,112662.29799999998,119290.033803,103353.98833129661,128803.56000000001,132236.64000000001,116890.92,106260.78000000001,105427.86,83446.760000000184,101154.24000000002,139685.16]
[null,"ARJ09",1318.9939999999999,2723.3510000000001,11117.340999999999,10227.266529,11031.299359000001,8515.6443321999977,9389.0358410000008,9982.8344514499986,5243.730669999999,10782.301104999993,8423.3989699999547,10825.283039999975,697.1232500000001]
[null,"ARJ11",745.93999999999994,4236.9679999999998,11709.505000000001,10111.723778,10810.116693,5377.4900456449959,6762.7585799999997,8208.257778800009,9655.3631199999982,7515.143299999977,4874.0930399999925,10874.30593000001,657.71189500000003]
[null,"ARJ12",null,4424.884,11000.347999999998,10451.810779000001,10819.399785999998,5023.2107812749982,6196.9345160000003,11548.431087550014,11349.074575000001,9975.9341299999905,7073.2160740378231,0,0]
[null,"ARJ13",null,4361.0770000000002,11177.776000000002,6701.477245,7067.3248859999994,2147.3923148100002,8851.2839679999997,10087.290187999994,9758.3664000000153,4970.5611999999865,5371.6201999999894,0,0]
[null,"ARJ14",null,390.226,105.83199999999999,8409.2019340000006,11050.091172999999,8526.9006409999947,10123.336069999999,9538.6528150000031,2570.0208000000066,7007.9093999999996,0,0,0]
[null,"ARJ15",null,404.85,92.990000000000009,2116.11598,12065.507664999999,7797.8295384000085,4892.938408,11580.990529000033,10493.689199999977,9947.2014000000054,7564.2671999999584,8339.7395999998589,474.07699999999943]
["KARACHIPAMPA","KAR1",2975.636,42228.252000000008,69735.072,78411.454968999999,96307.514407999988,80691.735044999994,79540.577999999994,60267.497718999999,84986.583595136995,61003.532321999912,79662.397554113864,76545.155212149999,41016.303]
["KENKO","KEN01",13972.6,19971.689999999999,33194.110000000008,33335.079999999994,32685.739999999998,46977.265625,50444.303124999999,50792.947500000002,25340.758313000002,43520.745187,0,1793.82,18.810000000000002]
[null,"KEN02",14438.369999999999,21892.86,33380.35,183.07,38581.040000000001,47451.323000000004,50578.209750000002,52201.957000000002,20555.564869999998,46932.179499999998,29966.794000000005,14728.669187500001,14455.24559]
["VALLE HERMOSO","VHE12345678",144010.66999999998,152904,182593.93999999997,182003.13,332553.04000000004,412298.62000000005,375505.48,441361.19300000003,438893.55500000005,458878.51799999998,260568.35899999994,431717.94459999999,498992.92799999996]
["CARRASCO","CAR123",532202.73,664769.48,648613.31000000006,664563.12,622012.59,743118.82019999996,616986.26712799992,772580.19999999972,667630.60999999987,815783.94000000006,516330.15,440398.8600000001,552699.28999999992]
["C.EL ALTO","ALT01",{"$nulls":7},57810.708899999998,107684.09799999998,108265.76249999998,62901.071699999942,100635.927,49236.522900000004]
[null,"ALT02",{"$nulls":8},103575.98907,74350.106548000011,230006.70250000007,213864.51399999997,148687.6958000001]
["BULO BULO","BUL01",262129,318460,118841,322794,303179,320717,327166,106480,287973.53399999999,269807.61800000013,253280.23099999985,223504.63100000005,237695.82099999994]
[null,"BUL02",286578,90205,321264,310832,327497,331746,326073,289542,202260.81000000006,173568.66000000032,33037.908999999891,15850.489000000001,77027.985999999757]
[null,"BUL03",{"$nulls":8},917.24761999999998,265758.58129,313954.44199999998,125500.57599999997,239710.45899999986]
["GUABIRA","GBE",null,null,14200.63,39318.21,59670.27,58156.17,64040.52,64494.2,79491,65694,62146,50538,29748]
[null,"IAG",{"$nulls":12},3137]
["ENTRE RIOS","ERI01",{"$nulls":5},94768,186730,193238,176801,173128,75240,152450,36192]
[null,"ERI02",{"$nulls":5},123773.2823375,193364,193432,175773,165138,85293,168623,52744]
[null,"ERI03",{"$nulls":5},109541.1267625,170825,196674,195325,173443,74301,182321,60409]
[null,"ERI04",{"$nulls":5},77401.001000000004,187411,183871,186743,193663,89367,182872,46175]
["DEL SUR","SUR01",{"$nulls":9},84605.7,283458,327520.80560572003,321801.02243377001]
[null,"SUR02",{"$nulls":9},129537,256045,313178.53026025603,283832.34028472006]
[null,"SUR03",{"$nulls":9},108702.3,285112,329847.8391620898,326287.42484508501]
[null,"SUR04",{"$nulls":9},73180,279769,310140.64298799884,335050.79283362499]
["WARNES","WAR01",{"$nulls":10},198822,327476,341340.33600000001]
[null,"WAR02",{"$nulls":10},104963,303848,232234.96000000008]
[null,"WAR03",{"$nulls":10},135385,334360,332215.63199999998]
[null,"WAR04",{"$nulls":10},75984,328445,319457.85599999991]
[null,"WAR05",{"$nulls":10},91678,330964,332882.23199999996]
["ENDE GEN.","MOX",{"$nulls":6},17193.921097000002,78175.629795999994,59999.305699999997,92959.207999999999,86494.671699999992,89033.761099999989,89110.905199999994]
["Total Generación bruta",null,4188810.4219999993,4506326.59,4901261.5930000013,5372000.1457690001,5632658.0872996198,6085526.1650659963,6611423.3663270017,6940448.355742652,7347749.5893445034,7836447.9107113639,8334811.4947674423,8759264.8637782205,8981304.9314322006]
["Unidades MDL"]
[{"$f":"+A61","v":"GUARACACHI"},"GCH09",345725,354602.80700000003,335472.45600000006,383101.16399999993,280808.80416330742,304167.35200000001,362328.33600000001,345670.74,479429.598,420127.47135156026,459226.69199999992,240047.45999999993,381288.42]
[null,"GCH10",350449.69800000009,346771.51500000001,308409.01799999998,353846.016,338845.1554794985,274064.72799999994,328187.05200000003,425317.902,461289.34800000006,412122.105063011,378806.54399999999,386168.79599999997,365210.38799999998]
[null,"GCH12",0,0,0,0,0,85.295999999999992,1236.1020000000001,369449.51400000002,616226.28899999999,523552.59600000002,544179.25994216464,222713.652,361213.69200000004]
[{"$f":"+A42","v":"CHOJLLA"},"CHJ",109893.09999999999,91555.531999999992,131993.4,115486.92299999997,119762.48675236771,106123.25798427663,124388.162,135330.64200000002,141958.08270668716,127364.10300000003,130614.54000000001,50256.089999999975,127227.77000000002]
[{"$f":"+A43","v":"YANACACHI"},"YAN",179704.90000000002,131842.29999999999,215556.69999999998,197562.09999999992,197753.89600000007,190812.26330156953,206067.00099999999,209706.07100000003,223487.34744793986,70571.212,211398.55300000001,155757.26200000002,179334.13099999996]
["Total Unidades MDL",null,985772.69800000009,924772.1540000001,991431.57400000002,1049996.2029999997,937170.34239517362,875252.89728584606,1022206.6529999999,1485474.8689999999,1922390.6651546268,1553737.4874145715,1724225.5889421648,1054943.26,1414274.4010000001]
[]
[]
["Unidades LCMR "]
["Hidroelectricas",null,1941081.4510000001,2131353.7519999999,2294231.1209999998,2280487.4350000005,2264298.2447523675,2151428.9800358461,2324157.2736730007,2322431.2652733331,2514863.6186996265,2232992.8565349993,2439591.151326274,1715604.4612500006,2229863.9013999999]
["Eolicas",null,0,0,0,0,0,0,0,0,36.528500000000001,8157.7569999999996,11450.126,34911.444000000003,60383.278999999995]
["Solares",null,0,0,0,0,0,0,0,0,0,0,0,0,1065.63625]
["Biomasa",null,0,0,14200.63,39318.21,59670.27,58156.17,64040.52,64494.2,79491,76309.624999999985,79093.507500000007,61901.893750000003,44798.720000000001]
["Total Unidades LCMR",null,1941081.4510000001,2131353.7519999999,2308431.7509999997,2319805.6450000005,2323968.5147523675,2209585.150035846,2388197.7936730008,2386925.4652733332,2594391.1471996265,2317460.2385349995,2530134.784826274,1812417.7990000006,2336111.5366500001]

{"sheet":"Proyectos ","index":1,"n_rows":67,"n_cols":7,"rows_kept":67,"cut":false,"hidden":false,"merged":[[2,2,2,6]]}
[]
[]
[null,null,"Adiciones de proyectos (1999 - 2021)"]
[null,null,"Unidad","Fecha Puesta en Marcha","Capacidad (MW)","Tecnologia","Proyecto MDL"]
[null,null,"Palillada","2021-08-01",118.2,"Hydro","NO"]
[null,null,"Umapalca ","2021-07-01",85.8,"Hydro","NO"]
[null,null,"Sehuencas","2021-06-01",198.6,"Hydro","NO"]
[null,null,"Juntas","2021-06-01",91.56,"Hydro","NO"]
[null,null,"Warnes II","2021-05-01",24,"Eolico","NO"]
[null,null,"La Ventolera","2021-05-01",21,"Eolico","NO"]
[null,null,"Planta Piloto Goetermica","2020-12-01",5,"Geotermico","NO"]
[null,null,"CCSUR10","2020-02-01",36.72,"Thermal","NO"]
[null,null,"CCWAR20","2020-02-01",40.340000000000003,"Thermal","NO"]
[null,null,"CCERI50","2019-12-01",136.4,"Thermal","NO"]
[null,null,"CCSUR20","2019-12-01",36.72,"Thermal","NO"]
[null,null,"CCWAR10","2019-12-01",40.340000000000003,"Thermal","NO"]
[null,null,"CCERI40","2019-10-01",136.4,"Thermal","NO"]
[null,null,"CCERI30","2019-08-01",136.4,"Thermal","NO"]
[null,null,"CCWAR40","2019-08-01",135.15,"Thermal","NO"]
[null,null,"CCWAR30","2019-07-01",135.15,"Thermal","NO"]
[null,null,"AGU01","2019-05-01",4.57,"Biomass","NO"]
[null,null,"CCSUR40","2019-04-01",132.69,"Thermal","NO"]
[null,null,"CCSUR30","2019-02-01",132.69,"Thermal","NO"]
[null,null,"San José 2","2019-02-01",69,"Hydro","NO"]
[null,null,"Warnes I","2020-05-01",14.4,"Eolico","NO"]
[null,null,"San Julian","2020-07-01",39.6,"Eolico","NO"]
[null,null,"El Dorado","2020-08-01",54,"Eolico","NO"]
[null,null,"Yunchara","2017-10-01",5,"Solar","NO"]
[null,null,"IAG01","2017-07-01",5,"Biomasa","NO"]
[null,null,"Misicuni","2017-09-01",120,"Hidro","NO"]
[null,null,"SBU01","2016-09-01",12,"Biomasa","NO"]
[null,null,"QOLLPANA II","2016-08-01",24,"Eolico","NO"]
[null,null,"WAR01","2015-09-01",40,"Termico","NO"]
[null,null,"WAR02","2015-09-01",40,"Termico","NO"]
[null,null,"WAR03","2015-09-01",40,"Termico","NO"]
[null,null,"WAR04","2015-09-01",40,"Termico","NO"]
[null,null,"WAR05","2015-09-01",40,"Termico","NO"]
[null,null,"San Jacinto","2015-08-01",7,"Hidro","NO"]
[null,null,"UNA01","2015-06-01",6,"Biomasa","NO"]
[null,null,"SUR01","2014-09-01",40,"Termico","NO"]
[null,null,"SUR02","2014-09-01",40,"Termico","NO"]
[null,null,"SUR03","2014-09-01",40,"Termico","NO"]
[null,null,"SUR04","2014-09-01",40,"Termico","NO"]
[null,null,"QOLLPANA I","2014-01-01",3,"Eolico","NO"]
[null,null,"BUL03","2013-12-01",50,"Termico","NO"]
[null,null,"ALT2","2013-03-01",32.35,"Termico","NO"]
[null,null,"ALT 1","2012-10-01",17.5,"Termico","NO"]
[null,null,"Ciclo Comb. (GCH 12)","2012-08-01",82,"Termico","SI"]
[null,null,"VHE 5,6,7,8","2012-08-01",42,"Termico","NO"]
[null,null,"Car 03","2012-01-01",25,"Termico","NO"]
[null,null,"Moxos","2011-10-01",28,"Termico","NO"]
[null,null,"ERI01","2010-05-01",26.782499999999999,"Termico","NO"]
[null,null,"ERI02","2010-05-01",26.782499999999999,"Termico","NO"]
[null,null,"ERI03","2010-05-01",26.782499999999999,"Termico","NO"]
[null,null,"ERI04","2010-05-01",26.782499999999999,"Termico","NO"]
[null,null,"Arj 13-14-15","2008-08-01",4.8,"Termico","NO"]
[null,null,"QUEHATA","2007-10-07",1.8,"Hidro","NO"]
[null,null,"Guabira Energia (GE)","2007-10-01",16.600000000000001,"Biomasa","NO"]
[null,null,"GCH 11","2007-05-07",60,"Termico","NO"]
[null,null,"Arj 9-10-11-12","2006-08-01",6.4,"Termico","NO"]
[null,null,"Santa Isabel SIS5 ","2004-06-04",21.3,"Hidro","NO"]
[null,null,"Chojlla","2002-06-01",38.4,"Hidro","SI"]
[null,null,"Yanacachi","2002-06-01",80,"Hidro","SI"]
[null,null,"Landara LAN1and3 ","2001-06-23",5,"Hidro","NO"]
[null,null,"Kilpani  KIL3 ","2001-05-01",5,"Hidro","NO"]
[null,null,"CECBB1 & 2","2000-05-01",85.88,"Termico","NO"]
[null,null,"Huaji","1999-06-01",29,"Hidro","NO"]

{"sheet":"Eficiencia","index":2,"n_rows":75,"n_cols":34,"rows_kept":75,"cut":false,"hidden":false,"merged":[[11,15,12,17],[4,0,4,20],[6,0,6,20],[7,0,7,20],[9,0,9,20],[11,0,12,0],[11,1,12,1],[11,2,12,2],[11,3,12,3],[11,4,12,4],[11,5,12,5],[11,6,12,6],[11,7,12,8],[11,9,11,11],[11,12,12,12],[11,13,12,14],[11,32,12,32],[11,33,12,33],[12,18,12,20],[12,21,12,23],[12,24,12,26],[12,30,13,30],[11,18,11,20],[11,21,11,23],[11,24,11,26],[11,27,12,28],[11,29,12,29],[11,31,13,31]]}
["CNDC",{"$nulls":19},"Informe de Precios de Nodo mayo - octubre 2018"]
[]
[]
[]
["ANEXO 5F"]
[]
["CARACTERISTICAS DE UNIDADES TERMICAS PARA LA TEMPERATURA MEDIA ANUAL"]
["TURBINAS A GAS"]
[]
["Periodo mayo - octubre 2018"]
[" ",{"$nulls":19},"Página 1 de 4"]
["UNIDAD","FOR","TEMP","POTENCIA EN BORNES"," CP&T     (1)","POTENCIA INYECTADA","PODER CALORIFICO","COSTO DE COMBUSTIBLE",null,"RENDIMIENTO TERMICO",null,null,"O&M","REPRESENTACION LINEAL DE COSTO",null,"COSTO (US$/MWh)",null,null,"RENDIMIENTO TERMICO",null,null,"Eje X",null,null,"Eje Y",null,null,"Estimacion Lineal",null,"(MMBTU/MWh)","Eficiencia (%)","Tipo de Combustible","Factor de Emisiones","Factor de Emisiones"]
[{"$nulls":9},"50% (2)",0.75,1,{"$nulls":6},"(MMBTU/MWh)",null,null,"% carga",null,null,"RENDIMIENTO TERMICO",{"$nulls":5},"ηm,y"]
[null,"%"," °C","MW","%","MW"," BTU/PC","US$/MPC","US$/MMBTU","BTU/KWh","BTU/KWh","BTU/KWh","US$/MWh","a","b","Al 93%","Al 92%","Al 90%","Al 93%","Al 92%","Al 90%",null,null,null,{"$f":"+J14","v":"BTU/KWh"},{"$f":"+K14","v":"BTU/KWh"},"BTU/KWh","a","b",{"$f":"1-'[16]% despacho'!G9","v":0.91428571428571426},null,null,"EFCO2 (tCO2/TJ)","EFEL,m,y"]
[]
["GCH01",11.95,26,18.62,3.5,17.970000000000002,925.6,1.131,1.2219101123595506,16761,14443,12977,3.1349999999999998,90.31159812008373,14.761175351123637,20.165819164414106,20.224671910112367,20.346308197139944,13.937865798922807,13.98603034482759,14.085576363636367,0.5,0.75,1,{"$f":"+J16","v":16761},{"$f":"+K16","v":14443},12977,{"$f":"INDEX(LINEST(Y16:AA16,V16:X16),1,2)","v":20403},{"$f":"INDEX(LINEST(Y16:AA16,V16:X16),1,1)","v":-7567.9999999999991},{"$f":"AB16+AC16*$AD$14","v":13483.685714285715},{"$f":"3412/AD16","v":0.25304653878019784},"Gas Natural",54.3,{"$f":"((AG16*3.6)/1000)/AE16","v":0.77250612058281698}]
["GCH02",2.76,26,17.62,3.5,17,925.6,1.131,1.2219101123595506,18220,15214,13610,4.1399999999999997,103.10254095716307,15.522092696629217,22.043442535791964,22.11432677317417,22.26082086376406,14.652012741935492,14.71002375000001,14.829913166666678,{"$f":"+V16","v":0.5},{"$f":"+W16","v":0.75},1,{"$f":"+J17","v":18220},15214,13610,{"$f":"INDEX(LINEST(Y17:AA17,V17:X17),1,2)","v":22596.333333333336},{"$f":"INDEX(LINEST(Y17:AA17,V17:X17),1,1)","v":-9220},{"$f":"AB17+AC17*$AD$14","v":14166.61904761905},{"$f":"3412/AD17","v":0.24084786839619626},"Gas Natural",{"$f":"+AG16","v":54.3},{"$f":"((AG17*3.6)/1000)/AE17","v":0.81163267626863178}]
["GCH04",1.39,26,19.95,3.5,19.25,925.6,1.131,1.2219101123595506,16884,13887,12867,4.1399999999999997,99.338020241396848,15.332391151685385,20.882001221037164,20.941539668986167,21.064533115989878,13.7014998498603,13.750225568181781,13.850882274235394,{"$f":"+V17","v":0.5},0.75,1,{"$f":"+J18","v":16884},13887,12867,20571.5,-8034.0000000000018,13226.12857142857,0.25797420473975219,"Gas Natural",{"$f":"+AG17","v":54.3},0.75775017970189229]
["GCH06",3.42,26,20.71,3.5,19.990000000000002,925.6,1.131,1.2219101123595506,16387,13684,12598,4.0650000000000004,98.080469729810162,15.205539396067447,20.481519478359548,20.5388982720767,20.657483238747275,13.435128584588503,13.482086861745527,13.579135708032251,0.5,0.75,1,16387,13684,12598,19906.5,-7577.9999999999991,12978.042857142858,0.26290558889024646,"Gas Natural",54.3,0.74353687506280364]
["GCH09",3.06,26,50.84,3.5,49.06,925.6,1.131,1.2219101123595506,16181,13345,11934,10.624000000000001,272.99085136938305,20.345571839887679,26.328277326834492,26.393220297339671,26.52883008154981,12.852236157133515,12.905384887018212,13.016366687429269,0.5,0.75,1,16181,13345,11934,20190.5,-8494,12424.557142857142,0.27461743390681359,"Gas Natural",54.3,0.71182662083403103]
["GCH10",3.27,26,51.85,3.5,50.04,925.6,1.131,1.2219101123595506,16181,13345,11934,10.624000000000001,278.41415506495747,20.345571839887644,26.327826998137699,26.3927950167981,26.527058408825418,12.851867612269013,12.905036841333617,13.01491676676287,0.5,0.75,1,16181,13345,11934,20190.5,-8494,12424.557142857142,0.27461743390681359,"Gas Natural",54.3,0.71182662083403103]
["GCH11",2.54,26,62.22,3.5,60.04,925.6,1.131,1.2219101123595506,13827,11267,10242,10.624000000000001,278.75295148525316,19.042954564606696,24.03494868146295,24.089170196128293,24.201225317479622,10.975397081840942,11.019771470854419,11.111476351776426,0.5,0.75,1,13827,11267,10242,17156.166666666664,-7169.9999999999982,10600.738095238095,0.32186438051258787,"Gas Natural",54.3,0.60733654245520008]
["GCH09COM",5.79,26,103.96,3.5,100.32,925.6,1.131,1.2219101123595506,7636,7378,7218,3.008,55.636183403092929,11.607803370786511,12.204118305439168,12.210644235485752,12.223997671407764,7.5260186591640084,7.5313594203055816,7.5422877494739389,0.5,0.75,1,7636,7378,7218,8037.666666666667,-836.00000000000011,7273.3238095238094,0.46911152168589981,"Gas Natural",54.3,0.41670261966169819]
["GCH10COM",5.92,26,102.87,3.5,99.27000000000001,925.6,1.131,1.2219101123595506,7636,7378,7218,3.008,55.052849044592428,11.607803370786495,12.204129725255651,12.210593790633123,12.224020619998409,7.5260280050368094,7.5313181367020503,7.5423065303895029,0.5,0.75,1,7636,7378,7218,8037.666666666667,-836.00000000000011,7273.3238095238094,0.46911152168589981,"Gas Natural",54.3,0.41670261966169819]
["SCZ01",0.6,26,20.76,2.2999999999999998,20.28,925.6,1.131,1.2219101123595506,16152,13915,12683,3.1349999999999998,90.512454482443758,14.652629410112384,19.451805151493282,19.503243262333378,19.612215957095604,13.353523296394503,13.395619773311914,13.484802024657549,0.5,0.75,1,16152,13915,12683,19453.5,-6938.0000000000009,13110.185714285713,0.26025565726975647,"Gas Natural",54.3,0.75110759186065978]
["SCZ02",2.2400000000000002,26,21.19,2.2999999999999998,20.700000000000003,925.6,1.131,1.2219101123595506,16523,14234,12816,3.1349999999999998,99.397667856846383,14.521377935393263,19.684893148735934,19.741843684177212,19.856733161203589,13.544280369999981,13.590888164522042,13.684912656065464,0.5,0.75,1,16523,14234,12816,20084.833333333336,-7414,13306.31904761905,0.25641952427185505,"Gas Natural",54.3,0.76234444531904211]
["GBE01",12.65,26,21,1.7,20.64,{"$nulls":6},2.0830000000000002,0,2.0830000000000006,2.0830000000000006,2.0830000000000006,2.0830000000000006,0,0,0,{"$nulls":10},"Biomasa"]
["IAG01",3,26,5,0,5,{"$nulls":6},3.5,0,3.5,3.5,3.5,3.5,0,0,0,{"$nulls":10},"Biomasa"]
["UNA01",5,26,14.57,0,14.57,{"$nulls":6},3.5,-9.1398651707316319E-14,3.5000000000000084,3.5000000000000018,3.5000000000000013,3.5000000000000018,0,0,0,{"$nulls":10},"Biomasa"]
["SBU01",5.25,26,6,0,6,{"$nulls":6},3.5,0,3.5,3.5,3.5000000000000004,3.5,0,0,0,{"$nulls":10},"Biomasa"]
["BUL01",11.34,26,44.82,2.6,43.65,925.4,1.131,1.2221741949427276,10516,9420,8715,4.1269999999999998,102.69055155139424,12.796815305813668,15.326762375323259,15.353850952013726,15.410471491901584,9.1638020354766958,9.1859662873505759,9.2322940040722585,{"$f":"+V26","v":0.5},{"$f":"+W26","v":0.75},1,10516,9420,8715,12251.833333333334,-3601.9999999999995,8958.5761904761912,{"$f":"3412/AD31","v":0.38086409351826206},{"$f":"+AF26","v":"Gas Natural"},{"$f":"+AG26","v":54.3},{"$f":"((AG31*3.6)/1000)/AE31","v":0.51325394891977894}]
["BUL02",13.35,26,44.82,2.6,43.65,925.4,1.131,1.2221741949427276,10516,9420,8715,4.1269999999999998,102.69055155139424,12.796815305813668,15.326762375323259,15.353850952013726,15.410471491901584,9.1638020354766958,9.1859662873505759,9.2322940040722585,0.5,0.75,1,10516,9420,8715,12251.833333333334,-3601.9999999999995,8958.5761904761912,0.38086409351826206,{"$f":"+AF31","v":"Gas Natural"},{"$f":"+AG31","v":54.3},0.51325394891977894]
["BUL03",4.74,26,49.02,2.6,47.75,925.4,1.131,1.2221741949427276,10179,9015,8535,4.1269999999999998,100.00951712690672,12.767974439161463,15.019933843054883,15.044539818786019,15.094859435134167,8.9127506439991055,8.9328835970862777,8.9740558101442574,0.5,0.75,1,10179,9015,8535,11709,-3288,8702.8285714285721,0.39205644141970258,{"$f":"+AF32","v":"Gas Natural"},54.3,0.498601679115726]
["CAR01",1.38,26,53.65,2.5,52.309999999999995,929.5,1.131,1.2167832167832169,11489,10175,9745,3.0150000000000001,114.1637577709795,12.993869580419576,15.340503861426347,15.365857067869804,15.418758233159156,10.129580759677975,10.150417015548172,10.193893260584822,{"$f":"+V33","v":0.5},0.75,1,11489,10175,9745,13085.666666666668,-3488.0000000000009,9896.638095238095,0.34476354163559153,"Gas Natural",54.3,0.56699730798861159]
["CAR02",2.85,26,55.39,2.5,54.01,929.5,1.131,1.2167832167832169,11482,10271,9933,3.0150000000000001,103.92895905856406,13.471548251748258,15.540609750027455,15.563095022900685,15.609564278462186,10.294035599160493,10.312514875142515,10.350705125402829,0.5,0.75,1,11482,10271,9933,12885.5,-3097.9999999999995,10053.042857142857,0.33939972687729231,"Gas Natural",54.3,0.57595803567241666]
["CAR03",5.07,26,24.32,2.5,23.71,929.5,1.131,1.2167832167832169,11619,10356,9749,5.25,56.596932139860193,15.076710839160805,17.643465131217958,17.67171002026398,17.728863235592865,10.18543398715039,10.208646740791661,10.255617486722871,0.5,0.75,1,11619,10356,9749,13379.666666666664,-3739.9999999999991,9960.2380952380936,0.34256209212822419,"Gas Natural",54.3,0.57064107352202298]
["VHE01",8.9700000000000006,18,18.52,0.7,18.39,929.9,1.131,1.2162598128831057,14467,12428,11519,2.1680000000000001,66.451175264383068,12.665534796214665,16.551568437406658,16.592909220823593,16.680711549349596,11.826065685185192,11.860055777580778,11.932246215508567,0.5,0.75,1,14467,12428,11519,17226.666666666664,-5896,11836.038095238093,0.28827213739475249,"Gas Natural",54.3,0.67810923999330075]
["VHE02",0.52,18,18.809999999999999,0.7,18.68,929.9,1.131,1.2162598128831057,14152,12315,11560,1.2669999999999999,59.086690007374955,12.250769927949188,15.65242162670422,15.688041016219984,15.765742563724023,11.827589363989615,11.856875367801029,11.920761016805455,0.5,0.75,1,14152,12315,11560,16563.666666666664,-5184,11824.009523809522,0.28856539679957088,"Gas Natural",54.3,0.6774201001507284]
["VHE03",10.65,18,18.32,0.7,18.190000000000001,929.9,1.131,1.2162598128831057,14815,12533,11435,1.2669999999999999,75.679138292160417,11.13255160232278,15.605313912734152,15.656110376510492,15.755589983028976,11.788857743104764,11.830622227336081,11.912413638566441,0.5,0.75,1,14815,12533,11435,17997.666666666664,-6760,11817.095238095237,0.28873423893552119,"Gas Natural",54.3,0.67702396750962979]
["VHE04",2.0099999999999998,18,18.63,0.7,18.5,929.9,1.131,1.2162598128831057,14044,12173,11383,1.2669999999999999,60.164129494938258,11.949475614582198,15.445357630557691,15.484383340489265,15.562936845509421,11.657342847617681,11.689429503378397,11.754015625675695,0.5,0.75,1,14044,12173,11383,16524.833333333336,-5322.0000000000009,11659.004761904764,0.292649335829122,"Gas Natural",54.3,0.66796666203316035]
["VHE05",2.66,18,10.58,0.7,10.51,929.9,1.131,1.2162598128831057,12381,10642,9861,8.1289999999999996,32.463292606479413,17.120063229379483,20.442815799131722,20.477177252800313,20.551700925624662,10.124330072159673,10.152581810237853,10.213854633720931,0.5,0.75,1,12381,10642,9861,14741.333333333334,-5040,10133.333333333334,0.33671052631578946,"Gas Natural",54.3,0.58055803048065646]
["VHE06",3.27,18,10.58,0.7,10.51,929.9,1.131,1.2162598128831057,12381,10642,9861,8.1289999999999996,32.463292606479413,17.120063229379483,20.442815799131722,20.477177252800313,20.551700925624662,10.124330072159673,10.152581810237853,10.213854633720931,0.5,0.75,1,12381,10642,9861,14741.333333333334,-5040,10133.333333333334,0.33671052631578946,"Gas Natural",54.3,0.58055803048065646]
["VHE07",2.59,18,10.58,0.7,10.51,929.9,1.131,1.2162598128831057,12381,10642,9861,8.1289999999999996,32.463292606479413,17.120063229379483,20.442815799131722,20.477177252800313,20.551700925624662,10.124330072159673,10.152581810237853,10.213854633720931,0.5,0.75,1,12381,10642,9861,14741.333333333334,-5040,10133.333333333334,0.33671052631578946,"Gas Natural",54.3,0.58055803048065646]
["VHE08",2.89,18,10.58,0.7,10.51,929.9,1.131,1.2162598128831057,12381,10642,9861,8.1289999999999996,32.463292606479413,17.120063229379483,20.442815799131722,20.477177252800313,20.551700925624662,10.124330072159673,10.152581810237853,10.213854633720931,0.5,0.75,1,12381,10642,9861,14741.333333333334,-5040,10133.333333333334,0.33671052631578946,"Gas Natural",54.3,0.58055803048065646]
["ARJ08",0.28999999999999998,15,18.39,2.9,17.86,965.4,1.131,1.1715351149782474,14347,12590,11586,1.389,61.67320679620088,12.027622513983841,15.740639178414961,15.781317388980852,15.865407628868775,12.250285113034309,12.285007256695062,12.356785079495946,0.5,0.75,1,14347,12590,11586,16982.5,-5522.0000000000009,11933.814285714285,0.28591026459029389,"Gas Natural",54.3,0.68371102478646772]
["ARJ09",17.66,15,1.49,2.9,1.45,965.4,1.131,1.1715351149782474,10136,9773,9360,15.452999999999999,2.1127820878806856,25.324131115599766,26.889154884400273,26.912689076412313,26.936941869707159,9.7616834000000221,9.7817717368421295,9.8024734580152888,0.6,0.75,1,10136,9773,9360,11252.979591836734,-1910.612244897959,9506.1341107871722,0.3589261376113137,"Gas Natural",54.3,0.5446245885043014]
["ARJ11",17.329999999999998,15,1.49,2.9,1.45,965.4,1.131,1.1715351149782474,10318,9920,9476,15.452999999999999,2.2888472618707425,25.345362846488449,27.040805262688998,27.066300637368705,27.092574496771459,9.8911292666666313,9.912891631578912,9.9353184961831715,0.6,0.75,1,10318,9920,9476,11527.285714285714,-2071.4285714285706,9633.4081632653069,0.35418409997521377,"Gas Natural",54.3,0.55191636217910378]
["ARJ12",21.3,15,1.6,2.9,1.55,965.4,1.131,1.1715351149782474,10004,9154,9050,15.452999999999999,1.7368982796768373,25.21280599129895,26.418985352185643,26.427420172891143,26.453447619639547,9.3603556666666847,9.367555468531485,9.3897720000000167,{"$f":"+V45","v":0.5},0.75,1,10004,9154,9050,10833.666666666666,-1908.0000000000005,9089.2095238095226,0.37539018008795366,"Gas Natural",54.3,0.52073818221403434]
["ARJ13",22.37,15,1.55,2.9,1.51,965.4,1.131,1.1715351149782474,9587,9284,8846,15.452999999999999,2.1386583521597875,24.75210449347427,26.279717602159831,26.290707624524476,26.324647399474113,9.2414793750000896,9.2508602482015299,9.2798305919118569,{"$f":"+V47","v":0.6},0.75,1,9587,9284,8846,10682.091836734693,-1842.2448979591834,8997.7536443148674,0.37920575900139641,"Gas Natural",54.3,0.51549850011449894]
["ARJ14",23.51,15,1.51,2.9,1.47,965.4,1.131,1.1715351149782474,9792,9358,9037,15.452999999999999,2.0111373289464942,25.002801292728495,26.470784744514262,26.49253264750368,26.526390178294022,9.4045706386861792,9.4231342333333803,9.4520343750000446,{"$f":"+V49","v":0.6},0.75,1,9792,9358,9037,10825.969387755102,-1825.918367346939,9156.5583090379005,0.37262909106713332,"Gas Natural",54.3,0.52459672281674341]
["ARJ15",23.67,15,1.6,2.9,1.55,965.4,1.131,1.1715351149782474,10004,9154,9050,15.452999999999999,1.7368982796768373,25.21280599129895,26.418985352185643,26.427420172891143,26.453447619639547,9.3603556666666847,9.367555468531485,9.3897720000000167,{"$f":"+V48","v":0.5},0.75,1,10004,9154,9050,10833.666666666666,-1908.0000000000005,9089.2095238095226,0.37539018008795366,"Gas Natural",54.3,0.52073818221403434]
["KEN01",16,10,9.35,5,8.879999999999999,944,1.131,1.1980932203389831,15355,12990,12074,5.63,38.069600027144766,16.691575370762763,21.300485785671331,21.351257136631155,21.456231193934823,13.079521292372888,13.121898087515305,13.209515691489365,0.5,0.75,1,15355,12990,12074,18394.5,-6562,12394.957142857143,0.27527323900157552,"Gas Natural",54.3,{"$f":"((AG52*3.6)/1000)/AE52","v":0.71013078027131127}]
["KEN02",5.18,10,9.35,5,8.879999999999999,944,1.131,1.1980932203389831,15259,12731,11982,5.63,37.535396468485473,16.580871557203405,21.125108417794866,21.175167330579839,21.278668361769792,12.933140889830552,12.97492304161571,13.061311170212806,0.5,0.75,1,15259,12731,11982,18239.5,-6554.0000000000009,12247.271428571428,0.27859266612155009,"Gas Natural",54.3,0.70166958348685315]
["ALT01",4.67,10,17.5,1.3,17.27,944,1.131,1.1980932203389831,11396,10222,9682,7.335,36.237610909691981,17.005510067796639,19.261899290068868,19.28603938873383,19.337402661727911,9.9549009105437758,9.9750496754772175,10.017920524024001,0.5,0.75,1,11396,10222,9682,13004.333333333336,-3428.0000000000009,9870.161904761906,0.34568835171324441,"Gas Natural",54.3,0.56548043644280688]
["ALT02",7.51,10,32.35,1.3,31.93,944,1.131,1.1980932203389831,9522,8531,8140,6.0819999999999999,53.576507973054632,14.283971264830464,16.088501678203809,16.107541992299989,16.148150387066185,8.352022620888059,8.3679148017075047,8.4018089879668238,0.5,0.75,1,9522,8531,8140,10804,-2763.9999999999995,8276.914285714287,0.41223092111621995,"Gas Natural",54.3,0.47420023580639759]
["ERI01",0.93,26,28.72,2.6,27.97,930.7,1.131,1.2152143547867196,11812,10653,9767,7.1539999999999999,75.057350885440613,16.781866264102252,19.667577563042684,19.698980562020658,19.763882588513876,10.297424083044939,10.323265613680483,10.376673497020217,0.5,0.75,1,11812,10653,9767,13811.5,-4090.0000000000005,10072.071428571428,0.33875851895978276,"Gas Natural",54.3,0.57704821889130786]
["ERI02",0.77,26,28.04,2.6,27.31,930.7,1.131,1.2152143547867196,12203,10504,9728,7.1539999999999999,86.099095451876366,16.197112407865021,19.586840575261729,19.623260257123928,19.699923451472682,10.230985608661443,10.260955368085977,10.324041517493923,0.5,0.75,1,12203,10504,9728,14524.166666666668,-4950.0000000000009,9998.4523809523816,0.34125281293533521,"Gas Natural",54.3,0.57283044297437613]
["ERI03",1.41,26,29.13,2.6,28.369999999999997,930.7,1.131,1.2152143547867196,11869,10149,9786,7.1539999999999999,72.645199668130886,16.758176875470074,19.511975194959494,19.541517858923363,19.603660607085072,10.169378880591337,10.193689541379289,10.244826814336054,0.5,0.75,1,11869,10149,9786,13725.833333333334,-4166,9916.9190476190488,0.34405847054072569,"Gas Natural",54.3,0.56815924250544303]
["ERI04",1.54,26,28.44,2.6,27.700000000000003,930.7,1.131,1.2152143547867196,11974,10360,9872,7.1539999999999999,72.650143269495743,16.841713140646835,19.661982677506142,19.692974650438661,19.755878534529536,10.292820051242234,10.318323348508631,10.370086960288807,0.5,0.75,1,11974,10360,9872,13888.333333333336,-4204.0000000000009,10044.676190476192,0.33968242831312673,"Gas Natural",54.3,0.5754786933511975]
["KAR01",12.8,9,11.31,1.4,11.15,965.4,1.131,1.1715351149782474,15514,14023,13034,5.63,33.865456223446984,18.167482945929049,21.43319714298276,21.46820967336053,21.540536354638906,13.48930726952746,13.519193296783603,13.580929970617508,0.5,0.75,1,15514,14023,13034,17910.333333333332,-4959.9999999999991,13375.476190476191,0.2550937216298485,"Gas Natural",54.3,0.76630659018589853]
["SUR01",1.5,22,43.83,1.3,43.26,979.8,1.131,1.1543172075933865,11508,9681,8957,3.3980000000000001,129.12373618427057,10.888685260257214,14.098323246443407,14.133000239761499,14.205503554227688,9.2698291042133061,9.2998702342337012,9.362680797906533,0.5,0.75,1,11508,9681,8957,13875.166666666666,-5102,9210.4809523809527,0.37044753880284415,"Gas Natural",54.3,0.52768605409479152]
["SUR02",0.66,22,43.31,1.3,42.75,979.8,1.131,1.1543172075933865,11126,9741,9003,3.3980000000000001,107.8999700882252,11.442944519289671,14.156726463158515,14.186396593742385,14.246997796010701,9.3204245699405064,9.3461281896983106,9.3986277988782359,0.5,0.75,1,11126,9741,9003,13141.166666666666,-4246,9259.1095238095222,0.36850195920311174,"Gas Natural",54.3,0.53047207787640249]
["SUR03",0.6,22,44.16,1.3,43.589999999999996,979.8,1.131,1.1543172075933865,11572,9718,8917,3.3980000000000001,136.01269642817036,10.720302700551118,14.075327279440371,14.112140516714968,14.187360983196298,9.2499073991120024,9.2817991850374231,9.3469636528167381,0.5,0.75,1,11572,9718,8917,14051.5,-5310.0000000000009,9196.6428571428569,0.37100494745753498,"Gas Natural",54.3,0.52689324317534747]
["SUR04",0.71,22,44.06,1.3,43.49,979.8,1.131,1.1543172075933865,11478,9743,8934,3.3980000000000001,130.5655381615291,10.869976086956493,14.097801505041264,14.133298710338876,14.205835518778901,9.2693771128553752,9.3001288031742089,9.362968383111907,0.5,0.75,1,11478,9743,8934,13867.666666666664,-5087.9999999999991,9215.7809523809519,0.37023449424744515,"Gas Natural",54.3,0.52798970122257571]
["WAR01",0.64,26,44.58,1.3,44,911.2,1.131,1.2412203687445127,11555,9691,8883,3.306,148.61503061602261,11.11543956650571,14.747282934443701,14.786759492790855,14.868344380041634,9.217769239491691,9.2495738725296448,9.3153034474747454,0.5,0.75,1,11555,9691,8883,14051,-5344,9165.057142857142,0.37228354900756605,"Gas Natural",54.3,0.52508363724669227]
["WAR02",0.93,26,44,1.3,43.43,911.2,1.131,1.2412203687445127,11640,9739,8966,3.306,146.29884631584653,11.217285421422256,14.839440566652426,14.878417711608606,14.95990108568029,9.2920168384913282,9.3234191147813981,9.3890669047496722,{"$f":"+V65","v":0.5},0.75,1,11640,9739,8966,14126,-5348,9236.4000000000015,0.36940799445671468,"Gas Natural",54.3,0.52917100586166477]
["WAR03",0.61,26,44.33,1.3,43.75,911.2,1.131,1.2412203687445127,11536,9756,8964,3.306,142.44928675055991,11.343021044776089,14.843863678114989,14.882133759075714,14.960321368558715,9.2955803567624908,9.3264129807867278,9.389405509310965,0.5,0.75,1,11536,9756,8964,13943.333333333334,-5144,9240.2476190476191,0.36925417376982272,"Gas Natural",54.3,0.5293914433093283]
["WAR04",0.68,26,44.55,1.3,43.97,911.2,1.131,1.2412203687445127,11649,9800,8976,3.306,148.79042866720945,11.23111633999123,14.869913812899261,14.90949529344511,14.991299020486792,9.3165678747248517,9.3484570392459645,9.4143629243745046,0.5,0.75,1,11649,9800,8976,14151.166666666668,-5346.0000000000009,9263.3952380952396,0.36833147159351726,"Gas Natural",54.3,0.53071761463741429]
["WAR05",0.62,26,44,1.3,43.43,911.2,1.131,1.2412203687445127,11592,9787,8948,3.306,145.69028589881432,11.232373696224776,14.839461735314014,14.878276746745655,14.959421173810203,9.2920338932078952,9.323305545211884,9.3886802595719328,0.5,0.75,1,11592,9787,8948,14075,-5288.0000000000009,9240.2571428571428,0.36925379318448159,"Gas Natural",54.3,0.52939198894657502]
["MOS01",18.559999999999999,28,1.39,4.9000000000000004,1.3199999999999998,37289,0.46500000000000002,12.470165464346055,10530,9321,8918,21.405999999999999,28.70014973618218,116.97727329775522,140.31072836782201,140.69640531112893,141.09504618530326,9.5351363787262677,9.5660643519283575,9.598031920868328,0.5,0.75,1,{"$f":"+J70","v":10530},9321,8918,12007.666666666666,-3223.9999999999995,9060.0095238095237,0.37660004562173277,"Diesel Oil",72.599999999999994,0.69399885379333448]
[]
[]
[]
["1)  Consumo propio, ventas directas y pérdidas entre bornes de generador y el SMEC"]
["2) Los valores en negrilla corresponden al 60%"]